Cable Sizing Calculator — Safe Web Edition QA & Testing Master Document Manual Test Case Specification • AI Prompt Suite • Demo Script Version 1.0 ¦ March 2026 ¦ OC: 630276 ¦ Project: VSP – WWTP Area

📋 Document Contents PART A — AI Prompts (Pages 1-3): Two ready-to-use prompts — one for AI-assisted manual testing, one for generating a narrated demo video. PART B — Manual Test Cases (Pages 4+): 60 structured test cases across 7 modules covering all calculation logic, UI behaviour, validation, edge cases, and cross-module consistency. PART C — Test Execution Template: Empty Result and Status columns for recording test outcomes.

# PART A — AI Prompt Suite

## PROMPT 1 — Manual Testing Assistant

🎯 Purpose of this prompt Paste this prompt into any AI assistant (Claude, GPT-4, etc.) to get an intelligent manual testing partner that understands the Cable Sizing app deeply and can guide a QA tester through each test case, explain expected results, and flag deviations.

━━━ COPY THIS ENTIRE BLOCK AS YOUR PROMPT ━━━ You are a senior QA engineer and electrical engineering expert specialising in LT cable sizing software. You are helping me manually test the Cable Sizing Calculator — Safe Web Edition, a React web application that replaces an Excel-based cable sizing workbook. APPLICATION CONTEXT: - Stack: React 18 + Zustand state, .NET 8 backend (CableSizingEngine.Compute()), PostgreSQL, SignalR push updates. - Modules: Cable Schedule (main grid), Motor Calculator, Derating Factors, Cable Catalogue, Project Inputs. - Calculation standard: IS-1554, IS-732. Catalogue: POLYCAB LT-XLPE 3.5C Armoured, 17 sizes (1.5–400 mm²). - Key formula: FLC = P / (√3 × V × η × PF). VD_run = I × L × (R·cosφ + X·sinφ) / (runs × 1000). Required rating per cable = FLC / (DF × Runs). - Derating: F1 (air temp) × F2 (ground temp) × F3 (cable grouping: In Air or In Ground table) × F4 (laying: In Air=1.00, In Trench=1.00, In Duct=0.95, Underground=0.91). - Limits: Running VD ≤ 5%, Starting VD ≤ 15% of system voltage (415V AC, 3-phase). - Known bugs fixed: (v1.1) reqR now divides by runs; Air Temp column now visible; (v1.2) Section D F4 table added with ACTIVE badges. YOUR TESTING ROLE: When I describe a test case or paste a test case ID, you must: - State the expected numeric result (FLC, DF, VD%) computed from the formula with the given inputs. - Describe exactly what the tester should see on screen (cell colour, icon, popup content). - If I tell you what the app actually showed, compare it to expected and classify as PASS / FAIL / INCONCLUSIVE with a reason. - If FAIL: diagnose the most likely root cause from the source code patterns (calcDF, calcFLC, calcVD, pickCable, FMETA, GROUP_DF_AIR/GND, fDep mapping). - If asked, suggest the minimal code fix (function name + logic change). CALCULATION REFERENCE (use these to verify results): Air Temp DF: {25:1.14, 30:1.10, 35:1.04, 40:1.00, 45:0.95, 50:0.90, 55:0.85} Gnd Temp DF: {15:1.12, 20:1.08, 25:1.03, 30:1.00, 35:0.96, 40:0.91, 45:0.87} Group In Air: {1:1.00, 2:0.85, 3:0.79, 4:0.75, 5:0.70, 6:0.68, 9:0.63, 12:0.60} Group In Ground: {1:1.00, 2:0.90, 3:0.85, 4:0.80, 5:0.78, 6:0.75, 9:0.70, 12:0.67} F4: In Air=1.00, In Trench=1.00, In Duct=0.95, Underground=0.91. Starting PF = 0.20 (DOL). STARTING COMMAND: Reply "QA READY" then ask me which module I want to test first. I will paste test case IDs or describe what I am testing. Guide me through each case step by step.

## PROMPT 2 — Demo Video Script & Audio Generator

🎬 Purpose of this prompt Paste this prompt into an AI assistant to generate a complete narrated demo video script. The output will include: screen action directions (for screen recording), matching voiceover narration (for text-to-speech or live presenter), timestamps, chapter markers, and B-roll suggestions.

━━━ COPY THIS ENTIRE BLOCK AS YOUR PROMPT ━━━ You are a senior technical writer, product demo director, and electrical engineering educator. Create a complete narrated demo video script for the Cable Sizing Calculator — Safe Web Edition web application. VIDEO REQUIREMENTS: - Total duration: 8–10 minutes. Target audience: electrical project engineers and non-technical client managers. - Tone: Friendly, professional, confidence-building. Avoid jargon. When technical terms appear (impedance, derating), explain them in one simple sentence. - Format: For each scene, produce THREE components: (1) SCREEN ACTION — precise step-by-step mouse/keyboard instructions for the person recording, (2) VOICEOVER — exact words to be spoken or fed to text-to-speech, (3) VISUAL CUE — what the viewer should notice highlighted on screen. - Include: Opening hook (30s), Chapter titles on-screen, a mid-video 'gotcha' moment demonstrating the formula popup, and a closing call-to-action. APPLICATION MODULES TO COVER (in order): - INTRO (0:00–0:45): App header, project metadata, OC number. Voiceover explains the problem: 'Your engineers used to manage this in Excel...' - CABLE SCHEDULE (0:45–3:30): Show the 10 pre-loaded cables. Walk through Pump-01 (CB-015, 22kW, 50m, AL, In Air). Highlight Air Temp column. Show VD PASS icons. Click FLC blue cell to reveal formula popup — this is the 'aha moment'. - FAILURE DEMONSTRATION (3:30–4:15): Show CB-007 Conveyor Drive (700m cable). Highlight red FAIL icons on VD_run and VD_start. Explain what engineer must do: increase cable size or add parallel run. - MOTOR CALCULATOR (4:15–5:30): Switch to Motor Calculator tab. Enter same Pump-01 values. Show Section B (all 4 derating factors individually). Show Section C PASS verdict. - DERATING FACTORS (5:30–7:00): Navigate to Derating tab. Change Laying from In Air to In Duct. Show In Ground row highlighting and 'In Duct' badge in Section C. Scroll to NEW Section D table. Explain why 4 laying methods map to 2 grouping categories — this answers the 'why only 2 rows?' question. - CABLE CATALOGUE (7:00–7:45): Show read-only POLYCAB table. Point out 17 sizes, CU/AL split, impedance columns. Show admin banner. - CLOSE (7:45–8:30): Return to Cable Schedule. Add a new row live. Type inputs. Show auto-calculation. Final voiceover: 'Formulas that once lived in shared Excel sheets, fragile and editable by anyone, now live safely on the server. Engineers focus on decisions, not formulas.' Show next steps slide. AUDIO STYLE GUIDE: - Speaking pace: 130 words/minute (clear, not rushed). - Use 'we' for the app and team. Use 'you' for the engineer/viewer. - For each technical term introduced, immediately follow with a bracket: '(think of this as the cable's friction against current flow)'. - End each chapter with a one-sentence benefit statement. Example: 'That single click shows you exactly how the app reached that number — no more black box.' OUTPUT FORMAT: For each scene block use exactly this structure: [TIMESTAMP]: [CHAPTER TITLE] SCREEN ACTION: ... VOICEOVER: "..." VISUAL CUE: ... --- Begin immediately with the full script. Do not include preamble. Start with [0:00] OPENING HOOK.

# PART B — Manual Test Case Specification

## Test Case Summary Matrix

| Module | Total TCs | P1 Critical | P2 Standard |
| --- | --- | --- | --- |
| Cable Schedule | 32 | 20 | 12 |
| Motor Calculator | 7 | 5 | 2 |
| Derating Factors | 8 | 8 | 0 |
| Cable Catalogue | 4 | 2 | 2 |
| Project Inputs | 2 | 0 | 2 |
| Cross-Module | 2 | 1 | 1 |
| Edge Cases | 5 | 0 | 5 |
| TOTAL | 60 | 36 | 24 |

🔑 Priority Legend P1 — Critical: Must PASS before any release or client demo. Calculation correctness, data integrity, no-crash guarantees. P2 — Standard: Should PASS for complete feature coverage. UI behaviour, edge cases, cross-module consistency.

## Module: Cable Schedule  (32 Test Cases)

| TC-001 | Valid complete DOL motor entry | P1 — Critical | Input Validation |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | App open, Cable Schedule tab visible |
| Test Steps | 1. Click '+ Add Row' 2. Enter Tag=CB-016, Desc='Test Pump', kW=22, V=415, Feeder=DOL, m=50, η=91, PF=0.85, Is/In=6, Laying=In Air, Grp=3, Runs=1, Mat=AL, AirTemp=50°C 3. Tab out of last field |
| Expected Result | All blue cells populate: FLC≈39.57A, DF=0.711, ReqR=55.7A, Size=10mm², VD_run≈1.62% ✓, VD_start≈2.53% ✓. No red borders on any input. |
| Reference / Calculation | FLC=P/(√3·V·η·PF)=22000/(1.732×415×0.91×0.85)=39.57A |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-002 | kW = 0 — boundary guard | P1 — Critical | Input Validation |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | A row exists for editing |
| Test Steps | 1. Set kW field to 0 2. Tab out |
| Expected Result | Red validation border appears on kW cell. Calculated results show dashes or remain unchanged. No division-by-zero crash. |
| Reference / Calculation | FLC formula: kW=0 → FLC=0 or invalid; must be caught |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-003 | Cable length = 0 — boundary guard | P1 — Critical | Input Validation |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Valid row exists |
| Test Steps | 1. Set 'm' (length) field to 0 2. Tab out |
| Expected Result | VD_run = 0.00V (0.00%) ✓, VD_start = 0.00V (0.00%) ✓. Cable size still calculated. No crash. |
| Reference / Calculation | VD = I×L×Z/1000; L=0 → VD=0, valid mathematical edge case |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-004 | Efficiency η > 100% — invalid input | P1 — Critical | Input Validation |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Valid row exists |
| Test Steps | 1. Set η field to 105 2. Tab out |
| Expected Result | Red validation border on η field. Error message shown. FLC not recalculated with invalid efficiency. |
| Reference / Calculation | η physically cannot exceed 100%; input max constraint must be enforced |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-005 | Power factor PF > 1.0 — invalid input | P1 — Critical | Input Validation |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Valid row exists |
| Test Steps | 1. Set PF field to 1.2 2. Tab out |
| Expected Result | Red validation border on PF field. FLC not recalculated. Error indicator visible. |
| Reference / Calculation | PF is a ratio ≤ 1.0 by definition (IEEE/IS standard) |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-006 | Power factor PF = 0 — division-by-zero guard | P1 — Critical | Input Validation |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Valid row exists |
| Test Steps | 1. Set PF to 0 2. Tab out |
| Expected Result | Validation error shown. FLC not computed. App does not crash or show Infinity/NaN. |
| Reference / Calculation | FLC denominator includes PF; PF=0 causes divide-by-zero |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-007 | FLC correct: CU material, DOL, 11kW | P1 — Critical | Calculation — FLC |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | New row added |
| Test Steps | 1. Enter kW=11, V=415, η=90.6, PF=0.72, Mat=CU 2. Tab out |
| Expected Result | FLC = 11000/(1.732×415×0.906×0.72) = 23.46A ±0.05A |
| Reference / Calculation | FLC=P/(√3·V·η·PF). Cross-check with CB-008 in default data (23.46A shown) |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-008 | FLC correct: AL material, VFD feeder, 37kW | P1 — Critical | Calculation — FLC |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | New row added |
| Test Steps | 1. Enter kW=37, V=415, η=89, PF=0.85, Feeder=VFD, Mat=AL 2. Tab out |
| Expected Result | FLC = 37000/(1.732×415×0.89×0.85) = 68.2A ±0.1A. FLC is independent of feeder type. |
| Reference / Calculation | Cross-check with CB-013 in default data (121.12A is for 2 runs — single run: 68.2A ÷ check) |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-009 | FLC updates live when kW changed mid-row | P2 — Standard | Calculation — FLC |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Row with kW=22 exists, results visible |
| Test Steps | 1. Change kW from 22 to 30 2. Tab out |
| Expected Result | FLC changes from 39.57A to 53.87A. DF unchanged. New cable size selected if required. |
| Reference / Calculation | FLC recalculates on every input change without page reload (live reactive update) |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-010 | Air temp 25°C: F1 = 1.14 | P1 — Critical | Calculation — Derating |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Row with AirTemp=50°C exists |
| Test Steps | 1. Change AirTemp dropdown to 25°C 2. Tab out |
| Expected Result | F1 changes from 0.90 to 1.14. Combined DF increases. Smaller cable may be selected. |
| Reference / Calculation | POLYCAB XLPE table: 25°C → 1.14 (cable runs cooler, higher capacity allowed) |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-011 | Air temp 55°C: F1 = 0.85 (worst case) | P1 — Critical | Calculation — Derating |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Valid row exists |
| Test Steps | 1. Set AirTemp to 55°C 2. Tab out |
| Expected Result | F1 = 0.85. Combined DF is lowest for air. Larger cable size likely selected versus 25°C. |
| Reference / Calculation | POLYCAB XLPE: 55°C → 0.85. Verify: DF(55°C) < DF(25°C) by ratio 0.85/1.14 = 0.746 |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-012 | 3 cables In Air: F3 grouping = 0.79 | P1 — Critical | Calculation — Derating |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Valid row with Laying=In Air, Grp=3 |
| Test Steps | 1. Confirm Laying=In Air and Grp=3 2. Observe DF formula popup (click blue DF cell) |
| Expected Result | F3 Grouping = 0.79 shown in formula popup. Cross-reference: Derating tab Section C In Air row, column 3 = 0.79. |
| Reference / Calculation | POLYCAB grouping table In Air: {1:1.00, 2:0.85, 3:0.79, 4:0.75, 5:0.70, 6:0.68, 9:0.63, 12:0.60} |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-013 | In Duct laying: F4 = 0.95 applied | P1 — Critical | Calculation — Derating |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Valid row exists |
| Test Steps | 1. Set Laying = In Duct 2. Tab out 3. Click blue DF cell to open formula popup |
| Expected Result | F4 = 0.95 shown in popup. Combined DF = F1×F2×F3_InGround×0.95. Verify: DF(In Duct) = DF(In Trench) × 0.95 |
| Reference / Calculation | IS-1554: enclosed conduit reduces cable capacity. F4=0.95 for In Duct. |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-014 | Underground laying: F4 = 0.91 applied | P1 — Critical | Calculation — Derating |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Valid row exists |
| Test Steps | 1. Set Laying = Underground 2. Tab out 3. Click blue DF cell |
| Expected Result | F4 = 0.91 shown. Combined DF = F1×F2×F3_InGround×0.91. This is the most derated scenario for buried cables. |
| Reference / Calculation | IS-1554: direct buried cable — worst thermal dissipation. F4=0.91. |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-015 | Correct cable: 22kW AL In Air → 10mm² | P1 — Critical | Calculation — Cable Selection |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | New row added |
| Test Steps | 1. Enter kW=22, V=415, η=91, PF=0.85, Is/In=6, L=50, Laying=In Air, Grp=3, Runs=1, Mat=AL, AirTemp=50°C 2. Tab out |
| Expected Result | Size=10mm², Base=67A, Derated=47.64A, ReqR=55.7A per cable. Verdict: ADEQUATE (47.64A ≥ FLC 39.57A) |
| Reference / Calculation | POLYCAB: 10mm² AL In Air=67A. 67×0.711×1=47.64A ≥ 39.57A ✓ |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-016 | 200kW AL, 2 parallel runs — cable found (multi-run fix) | P1 — Critical | Calculation — Cable Selection |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Row CB-012 in default data visible |
| Test Steps | 1. Observe row CB-012: kW=200, Runs=2 2. Confirm no N/A in Size column |
| Expected Result | ReqR per cable = 305.7A. Cable selected = 400mm² AL (530A). Derated = 530×0.711×2 = 753.7A ≥ 434.75A ✓. No N/A shown. |
| Reference / Calculation | Bug fix v1.1: reqR = FLC/(DF×Runs) not FLC/DF. With 2 runs: 434.75/(0.711×2)=305.7A |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-017 | CU vs AL: same load, CU selects smaller size | P2 — Standard | Calculation — Cable Selection |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Two rows with identical inputs except material |
| Test Steps | 1. Add Row A: 22kW AL In Air → note Size 2. Add Row B: 22kW CU In Air → note Size |
| Expected Result | AL row → 10mm². CU row → selects from CU In Air catalogue. CU carries more current per mm², so smaller or equal size selected. |
| Reference / Calculation | CU has lower resistivity than AL. POLYCAB: 16mm² CU In Air=70A ≥ 55.7A required |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-018 | Short cable: VD_run < 1% — green PASS | P1 — Critical | Calculation — Voltage Drop |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | New row added |
| Test Steps | 1. Enter kW=22, L=20, η=91, PF=0.85, Mat=AL, In Air, Grp=3 2. Tab out |
| Expected Result | VD_run < 1%. Status icon = ✓ (green). VD_start also well within 15%. |
| Reference / Calculation | VD=I×L×(R·cosφ+X·sinφ)/1000. Short L minimises VD. |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-019 | Long cable: VD_run approaching 5% — amber warning | P2 — Standard | Calculation — Voltage Drop |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | New row added |
| Test Steps | 1. Increase cable length progressively until VD_run approaches 4.5% 2. Note status icon |
| Expected Result | When VD_run is between 4% and 5%, amber ⚠ warning indicator shown. Still PASS but flagged for review. |
| Reference / Calculation | Limit: 5% of 415V = 20.75V running voltage drop per IS-732 |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-020 | Very long cable (700m): VD_run >> 5% — red FAIL | P1 — Critical | Calculation — Voltage Drop |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Row CB-007 (Conveyor Drive, 700m) visible in default data |
| Test Steps | 1. Observe row CB-007: kW=5.5, L=700, PF=0.72 2. Check VD_run% value and status icon |
| Expected Result | VD_run ≈ 18.7% → ✗ red FAIL. VD_start similarly fails. Cable must be upsized or parallel run added. |
| Reference / Calculation | VD_run=12.61×700×(23.17×0.72+0.110×0.694)/1000=147.9V=35.6%≈FAIL (uses 1.5mm² selected) |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-021 | VD_start > 15% — red FAIL for starting | P1 — Critical | Calculation — Voltage Drop |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Identify a row where starting VD exceeds limit |
| Test Steps | 1. Observe CB-007 (700m DOL, Is/In=5) 2. Check VD_start% and icon |
| Expected Result | VD_start > 15% → ✗ red FAIL on VD_start column. VD_start = VD_run × Is/In × (cosφ_start/cosφ_run adjusted). |
| Reference / Calculation | Starting limit 15% per IS-732 Table 2. Starting PF assumed = 0.20 for DOL |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-022 | VFD: Is/In = 1, VD_start ≈ VD_run | P2 — Standard | Calculation — Voltage Drop |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | New row added |
| Test Steps | 1. Enter Feeder=VFD, Is/In=1, other fields normal 2. Observe VD_run vs VD_start |
| Expected Result | VD_start ≈ VD_run (within rounding). Both show ✓ PASS. VFD limits inrush to rated current. |
| Reference / Calculation | VFD eliminates DOL inrush. Is/In=1 means starting current = FLC. VD_start = VD_run × 1. |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-023 | 2 parallel runs halves required per-cable rating | P1 — Critical | Multi-Run Logic |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Row with high kW motor added |
| Test Steps | 1. Enter kW=100, Mat=AL, In Air, Grp=3, AirTemp=50°C 2. Note Size with Runs=1 3. Change Runs to 2, re-observe |
| Expected Result | With Runs=2: reqR per cable halves. App may select a smaller size. Derated rating = base × DF × 2. |
| Reference / Calculation | reqR = FLC/(DF×Runs). Doubling Runs halves reqR per cable. |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-024 | Derated rating formula: base × DF × runs | P1 — Critical | Multi-Run Logic |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Row with Runs=2 exists, cable selected |
| Test Steps | 1. Note Base rating, DF, and Runs 2. Manually verify: Derated = Base × DF × Runs |
| Expected Result | Derated A shown in blue cell equals Base × DF × Runs ±0.01A. |
| Reference / Calculation | Formula: I_derated = I_base × Combined_DF × N_runs |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-025 | Blue (calculated) cells cannot be edited by click | P1 — Critical | UI — Read-Only Enforcement |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Any row with results |
| Test Steps | 1. Click on any blue cell (FLC, DF, Size, VD%) 2. Attempt to type a value |
| Expected Result | Formula popup opens OR click is ignored. No text cursor appears in cell. Value cannot be overwritten. |
| Reference / Calculation | Core safety requirement: users edit inputs only, engine writes results. |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-026 | Click FLC blue cell: popup shows correct formula | P2 — Standard | UI — Formula Popup |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Valid row with calculated results |
| Test Steps | 1. Click FLC (blue) cell 2. Read popup content |
| Expected Result | Popup shows: formula text 'FLC = P / (√3 × V × η × PF)', actual substituted values, computed result matching cell value. |
| Reference / Calculation | FMETA.flc: label, expr, desc and live values displayed. |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-027 | Click reqR blue cell: shows per-run division | P2 — Standard | UI — Formula Popup |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Row with Runs=2 |
| Test Steps | 1. Click ReqR (blue) cell for a 2-run row 2. Read popup |
| Expected Result | Popup shows 'I_req = FLC ÷ (DF × 2 runs) = X A per cable'. Runs divisor explicitly shown. |
| Reference / Calculation | Bug fix v1.1: formula popup updated to show runs in denominator. |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-028 | Click VD_run blue cell: shows voltage in V and % | P2 — Standard | UI — Formula Popup |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Valid row with VD results |
| Test Steps | 1. Click VD_run (blue) cell |
| Expected Result | Popup shows formula: VD = I × L × (R·cosφ + X·sinφ) / (runs × 1000). Shows actual V value and % of 415V. |
| Reference / Calculation | VD formula per IS-1554 Appendix |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-029 | Add Row: new row appears with sensible defaults | P1 — Critical | UI — Row Operations |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Cable Schedule visible |
| Test Steps | 1. Click '+ Add Row' button 2. Observe new row |
| Expected Result | New row added at bottom with default values (kW=0 or blank, AL, In Air, 3 cables, 1 run, AirTemp=50°C). Row number auto-incremented. |
| Reference / Calculation | Default row: mk(id, 'CB-XXX', 'New Equipment', ...) |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-030 | Delete Row: row removed, remaining rows intact | P2 — Standard | UI — Row Operations |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Multiple rows exist |
| Test Steps | 1. Click delete (✕) on row 5 2. Observe remaining rows |
| Expected Result | Row 5 removed. Rows 1-4 and 6+ remain unaffected. No row renumbering of tag/IDs unless designed to. |
| Reference / Calculation | Row deletion should not affect other rows' calculations. |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-031 | 'Air Temp °C' column visible in Cable Schedule grid | P1 — Critical | UI — Column Visibility |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Cable Schedule tab open |
| Test Steps | 1. Scroll right on the Cable Schedule table 2. Look for column labelled 'Air Temp°C' |
| Expected Result | Column 'Air Temp°C' visible as 14th input column with dropdown per row. Default value = 50°C shown. |
| Reference / Calculation | Bug fix v1.2 — column was missing in v1.0 |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-032 | Changing Air Temp dropdown updates DF and cable results | P1 — Critical | UI — Column Visibility |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Row with results visible |
| Test Steps | 1. Change AirTemp from 50°C to 25°C in dropdown 2. Tab out or click away |
| Expected Result | F1 changes from 0.90 to 1.14. Combined DF increases. Cable size may decrease (less derating needed). VD values recalculate. |
| Reference / Calculation | calcDF() is reactive to airTemp input. |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

## Module: Motor Calculator  (7 Test Cases)

| TC-033 | Section B FLC matches Cable Schedule for identical inputs | P1 — Critical | Section B — Current Rating |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Both tabs accessible |
| Test Steps | 1. Note FLC for CB-004 in Cable Schedule (22kW, η=93.5, PF=0.72) 2. Open Motor Calculator 3. Enter same kW=22, V=415, η=93.5, PF=0.72 |
| Expected Result | FLC in Motor Calculator = FLC in Cable Schedule for CB-004 (45.46A ±0.05A). Calculation engine is the same. |
| Reference / Calculation | Both use calcFLC(kw, voltage, eff/100, pf). Must produce identical results. |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-034 | Section B shows all 4 derating factors individually | P1 — Critical | Section B — Current Rating |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Motor Calculator tab open |
| Test Steps | 1. Set Laying=In Duct, AirTemp=50°C, GndTemp=30°C, Cables in Group=6 2. Observe Section B |
| Expected Result | F1 Air Temp=0.90, F2 Ground=1.00, F3 Grouping=0.75 (6 cables In Ground), F4 Install=0.95 all shown with labels. |
| Reference / Calculation | Grouping In Ground: {6:0.75}. F4 In Duct=0.95. |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-035 | Combined DF = product of all four individual factors | P1 — Critical | Section B — Current Rating |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Motor Calculator with inputs set (TC-034 conditions) |
| Test Steps | 1. Manually compute: 0.90 × 1.00 × 0.75 × 0.95 2. Compare with Combined DF shown |
| Expected Result | Combined DF displayed = 0.6413 ±0.0001 (= 0.90×1.00×0.75×0.95). |
| Reference / Calculation | Combined DF = F1 × F2 × F3 × F4. All factors verified independently. |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-036 | Cable size auto-selected from POLYCAB catalogue | P1 — Critical | Section B — Current Rating |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Motor Calculator with valid inputs |
| Test Steps | 1. Enter kW=30, V=415, η=88, PF=0.88, Mat=AL, In Air, 6 cables 2. Observe cable selection |
| Expected Result | A cable size is shown with its base rating ≥ required per-run rating. Derated rating ≥ FLC. |
| Reference / Calculation | pickCable(reqPerRun, material, laying) scans POLYCAB array from smallest to largest. |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-037 | Section C: VD_run PASS for short cable | P1 — Critical | Section C — Voltage Drop |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Motor Calculator, reasonable inputs |
| Test Steps | 1. Set L=50m, all other inputs normal 2. Observe VD_run in Section C |
| Expected Result | VD_run < 5% → PASS verdict shown. Values match Cable Schedule for same conditions. |
| Reference / Calculation | VD = I × L × Z / 1000. L=50m produces low VD for most motor sizes. |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-038 | Section C: VD_start PASS with VFD (Is/In=1) | P1 — Critical | Section C — Voltage Drop |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Motor Calculator |
| Test Steps | 1. Set Feeder=VFD, Is/In=1 2. Observe VD_start |
| Expected Result | VD_start ≈ VD_run. PASS shown. Both within limits. Is/In=1 means no current multiplier at start. |
| Reference / Calculation | VD_start = VD_run × Is/In × adjusted_pf_factor. At Is/In=1: starting current = FLC. |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-039 | Section C: VD_start FAIL for long DOL motor | P1 — Critical | Section C — Voltage Drop |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Motor Calculator |
| Test Steps | 1. Set kW=22, L=400, Feeder=DOL, Is/In=7, PF=0.85, Mat=AL 2. Observe VD_start |
| Expected Result | VD_start > 15% → FAIL verdict in Section C. Cable must be upsized or parallel run added. |
| Reference / Calculation | DOL inrush: Is/In=7 multiplies VD by ~7. Starting PF=0.20. |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

## Module: Derating Factors  (8 Test Cases)

| TC-040 | Air temp 50°C selected: column 50 highlighted, F1=0.90 | P1 — Critical | Section A — Air Temp |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Derating Factors tab open |
| Test Steps | 1. Set Ambient Air Temp = 50°C in left panel 2. Observe Section A table |
| Expected Result | Column '50' highlighted in blue. XLPE Factor row shows 0.90 for that column. F1 in results = 0.9000. |
| Reference / Calculation | POLYCAB table: {25:1.14, 30:1.10, 35:1.04, 40:1.00, 45:0.95, 50:0.90, 55:0.85} |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-041 | Ground temp 30°C selected: column 30 highlighted, F2=1.00 | P1 — Critical | Section B — Ground Temp |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Derating Factors tab open |
| Test Steps | 1. Set Ground Temperature = 30°C 2. Observe Section B table |
| Expected Result | Column '30' highlighted. F2 = 1.0000 in results. This is the reference ground temperature (no derating). |
| Reference / Calculation | POLYCAB: {15:1.12, 20:1.08, 25:1.03, 30:1.00, 35:0.96, 40:0.91, 45:0.87} |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-042 | 'In Duct' selected: In Ground row highlights with 'In Duct' badge | P1 — Critical | Section C — Grouping |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Derating Factors tab, Laying = In Duct |
| Test Steps | 1. Set Laying Method = In Duct 2. Observe Section C table |
| Expected Result | 'In Ground' row highlighted (not In Air). Badge showing 'In Duct' appears next to 'In Ground' label. User understands In Duct maps to In Ground grouping. |
| Reference / Calculation | Bug fix v1.2 UX: badge shows actual selected method in the active row |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-043 | 'In Air' selected: In Air row highlighted only | P1 — Critical | Section C — Grouping |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Derating Factors tab |
| Test Steps | 1. Set Laying Method = In Air 2. Observe Section C |
| Expected Result | 'In Air' row highlighted. 'In Ground' row NOT highlighted. No badge on In Ground. Selected column also highlighted. |
| Reference / Calculation | In Air is the only method using the In Air grouping table. |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-044 | Section D visible with all 4 laying methods listed | P1 — Critical | Section D — NEW |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Derating Factors tab open |
| Test Steps | 1. Scroll down on Derating Factors tab 2. Find Section D: F4 Installation Method Factors |
| Expected Result | Table visible with 4 rows: In Air, In Trench, In Duct, Underground. Columns: Method, F3 Table Used, F4 Factor, Rationale. |
| Reference / Calculation | Added in v1.2 fix to explain why 4 dropdown methods map to 2 grouping rows. |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-045 | Section D: In Duct row shows ACTIVE + F4=0.95 | P1 — Critical | Section D — NEW |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Laying Method = In Duct |
| Test Steps | 1. Set Laying = In Duct 2. Observe Section D table |
| Expected Result | 'In Duct' row highlighted green with 'ACTIVE' badge. F4 column shows 0.95 highlighted. Other rows not highlighted. |
| Reference / Calculation | IS-1554: enclosed conduit = 5% capacity reduction |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-046 | Section D: Underground shows ACTIVE + F4=0.91 | P1 — Critical | Section D — NEW |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Laying Method = Underground |
| Test Steps | 1. Set Laying = Underground 2. Observe Section D |
| Expected Result | 'Underground' row highlighted green with 'ACTIVE' badge. F4 = 0.91 highlighted. Most derated scenario. |
| Reference / Calculation | IS-1554: direct burial = 9% capacity reduction |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-047 | Combined DF verified numerically: F1×F2×F3×F4 | P1 — Critical | Section D — NEW |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Derating tab, set AirTemp=50, GndTemp=30, Cables=2, Laying=In Duct |
| Test Steps | 1. Set conditions above 2. Read individual factors 3. Manually multiply: 0.90×1.00×0.90×0.95 |
| Expected Result | Combined DF = 0.7695. Results panel shows 0.7695. Matches 0.90×1.00×0.90×0.95. |
| Reference / Calculation | F1=0.90, F2=1.00, F3=0.90 (2 cables In Ground), F4=0.95 (In Duct). Product=0.7695 |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

## Module: Cable Catalogue  (4 Test Cases)

| TC-048 | 17 cable sizes visible from 1.5mm² to 400mm² | P2 — Standard | Data Completeness |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Cable Catalogue tab open |
| Test Steps | 1. Count rows in catalogue table |
| Expected Result | Exactly 17 rows visible: 1.5, 2.5, 4, 6, 10, 16, 25, 35, 50, 70, 95, 120, 150, 185, 240, 300, 400 mm². |
| Reference / Calculation | POLYCAB LT-XLPE 3.5C Armoured catalogue — 17 standard sizes |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-049 | CU and AL current ratings correct for In Air and In Ground | P1 — Critical | Data Accuracy |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Cable Catalogue tab open |
| Test Steps | 1. Check 10mm² row 2. Verify: AL In Air=67A, AL In Ground=53A, CU In Air=67A, CU In Ground=55A |
| Expected Result | Values match POLYCAB LT-XLPE 3.5C armoured published ratings. |
| Reference / Calculation | Embedded CATALOGUE array in source. Cross-verify with POLYCAB datasheet. |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-050 | Impedance R and X values shown for all sizes | P2 — Standard | Data Accuracy |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Cable Catalogue tab open |
| Test Steps | 1. Check 35mm² row for R_CU and X values |
| Expected Result | 35mm² shows R_CU=0.668 Ω/km, R_AL=1.100 Ω/km (approx), X≈0.082 Ω/km. All 17 rows have R and X values. |
| Reference / Calculation | POLYCAB impedance table (90°C conductor temp per IS-1554) |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-051 | Admin-only warning banner present; catalogue is read-only | P1 — Critical | Access Control |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Cable Catalogue tab open |
| Test Steps | 1. Look for admin warning banner 2. Attempt to click/edit any catalogue value |
| Expected Result | Banner text visible: 'Catalogue values are admin-managed'. No cell is editable by normal user. |
| Reference / Calculation | Role-based access: admin manages catalogue_polycab table. |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

## Module: Project Inputs  (2 Test Cases)

| TC-052 | OC No, Project Name, Revision fields are editable | P2 — Standard | Editable Fields |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Project Inputs tab open |
| Test Steps | 1. Edit OC No, Project Name, Revision fields 2. Switch to another tab and back |
| Expected Result | Values persist on return. Fields accept text input freely. |
| Reference / Calculation | Project metadata fields stored in project state. |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-053 | Voltage change in Project Inputs propagates to Cable Schedule | P2 — Standard | Cross-Module |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Project Inputs tab, Cable Schedule also visible |
| Test Steps | 1. Change System Voltage in Project Inputs 2. Switch to Cable Schedule 3. Observe FLC values |
| Expected Result | FLC in Cable Schedule recalculates for all rows using new voltage. Voltage used in FLC = V from project config. |
| Reference / Calculation | V is passed to calcFLC. Changing project voltage should trigger recompute. |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

## Module: Cross-Module  (2 Test Cases)

| TC-054 | Motor Calculator and Cable Schedule give identical FLC for same inputs | P1 — Critical | Calculation Consistency |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Both tabs accessible |
| Test Steps | 1. Set identical kW, V, η, PF in both Cable Schedule row and Motor Calculator 2. Compare FLC values |
| Expected Result | FLC values identical (same calculation engine used). Difference = 0 or rounding ≤0.01A. |
| Reference / Calculation | Both use calcFLC() from shared utility. No separate formula implementations. |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-055 | Derating tab selection reflects in Motor Calculator live | P2 — Standard | Calculation Consistency |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Derating Factors and Motor Calculator tabs |
| Test Steps | 1. Note conditions in Derating tab 2. Set Motor Calculator to matching conditions 3. Compare Combined DF |
| Expected Result | Combined DF in Motor Calculator = Combined DF shown in Derating Factors tab for identical inputs. |
| Reference / Calculation | Both use calcDF(airT, gndT, nCables, laying). Same result expected. |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

## Module: Edge Cases  (5 Test Cases)

| TC-056 | Maximum cable length 9999m — no crash or NaN | P2 — Standard | Boundary / Stress |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Valid row exists |
| Test Steps | 1. Set cable length = 9999 2. Tab out 3. Observe results |
| Expected Result | VD_run and VD_start computed (likely FAIL). App does not crash, freeze or show NaN/Infinity. |
| Reference / Calculation | Stress test: large L makes VD large but formula still valid. |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-057 | Non-standard group count interpolation (e.g. 7 cables) | P2 — Standard | Boundary / Stress |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Valid row exists |
| Test Steps | 1. Set Cables In Group = 7 (between 6 and 9 in standard table) 2. Observe DF grouping factor |
| Expected Result | App either: (a) interpolates between 0.68 (6 cables) and 0.63 (9 cables), or (b) uses nearest lower key. No crash. Factor is between 0.63 and 0.68. |
| Reference / Calculation | interpGroup() function handles non-key values. Verify behaviour is conservative (lower factor). |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-058 | Is/In = 1 (pure VFD): VD_start = VD_run | P2 — Standard | Boundary / Stress |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Valid row, Feeder=VFD, Is/In=1 |
| Test Steps | 1. Set Is/In=1 2. Compare VD_run and VD_start |
| Expected Result | VD_start numerically close to VD_run (only starting PF correction differs). Both PASS for reasonable length. |
| Reference / Calculation | VD_start = I × Is/In × L × Z_start / (runs×1000). At Is/In=1 and cosφ_s≈cosφ_run, values converge. |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-059 | Very large motor exceeding single-cable capacity — solved with parallel runs | P2 — Standard | Boundary / Stress |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | New row, large kW |
| Test Steps | 1. Enter kW=500, Runs=1, AL In Air 2. Note Size (likely N/A) 3. Set Runs=4 4. Note Size |
| Expected Result | With Runs=1: N/A (exceeds 530A max catalogue). With Runs=4: reqR per cable ≈125A → 50mm² or 70mm² selected. |
| Reference / Calculation | FLC for 500kW ≈ 869A. At DF=0.711, reqR=1221A single run (exceeds max). ÷4 runs = 305A → 185mm² |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

| TC-060 | Rapid sequential field changes — no stale or crossed results | P2 — Standard | Reactivity / Stability |
| --- | --- | --- | --- |

| FIELD | CONTENT |
| --- | --- |
| Pre-conditions | Row with results visible |
| Test Steps | 1. Rapidly change kW from 22→30→15→40 in quick succession 2. Pause, observe final result |
| Expected Result | Final result matches last value entered (kW=40). No stale intermediate results displayed. No frozen UI. |
| Reference / Calculation | React state batching must ensure only the latest input triggers the final calculation. |
| Actual Result | [Record here] |
| Status (PASS/FAIL/SKIP) | ☐ PASS ☐ FAIL ☐ SKIP ☐ BLOCKED |

# PART C — Test Execution Summary

Complete this table after executing all test cases.

| TC ID | Test Name | Priority | Tester | Date | Status | Defect Ref | Notes |
| --- | --- | --- | --- | --- | --- | --- | --- |
| TC-001 | Valid complete DOL motor entry | P1 |  |  |  |  |  |
| TC-002 | kW = 0 — boundary guard | P1 |  |  |  |  |  |
| TC-003 | Cable length = 0 — boundary guard | P1 |  |  |  |  |  |
| TC-004 | Efficiency η > 100% — invalid input | P1 |  |  |  |  |  |
| TC-005 | Power factor PF > 1.0 — invalid inp... | P1 |  |  |  |  |  |
| TC-006 | Power factor PF = 0 — division-by-z... | P1 |  |  |  |  |  |
| TC-007 | FLC correct: CU material, DOL, 11kW | P1 |  |  |  |  |  |
| TC-008 | FLC correct: AL material, VFD feede... | P1 |  |  |  |  |  |
| TC-009 | FLC updates live when kW changed mi... | P2 |  |  |  |  |  |
| TC-010 | Air temp 25°C: F1 = 1.14 | P1 |  |  |  |  |  |
| TC-011 | Air temp 55°C: F1 = 0.85 (worst cas... | P1 |  |  |  |  |  |
| TC-012 | 3 cables In Air: F3 grouping = 0.79 | P1 |  |  |  |  |  |
| TC-013 | In Duct laying: F4 = 0.95 applied | P1 |  |  |  |  |  |
| TC-014 | Underground laying: F4 = 0.91 appli... | P1 |  |  |  |  |  |
| TC-015 | Correct cable: 22kW AL In Air → 10m... | P1 |  |  |  |  |  |
| TC-016 | 200kW AL, 2 parallel runs — cable f... | P1 |  |  |  |  |  |
| TC-017 | CU vs AL: same load, CU selects sma... | P2 |  |  |  |  |  |
| TC-018 | Short cable: VD_run < 1% — green PA... | P1 |  |  |  |  |  |
| TC-019 | Long cable: VD_run approaching 5% —... | P2 |  |  |  |  |  |
| TC-020 | Very long cable (700m): VD_run >> 5... | P1 |  |  |  |  |  |
| TC-021 | VD_start > 15% — red FAIL for start... | P1 |  |  |  |  |  |
| TC-022 | VFD: Is/In = 1, VD_start ≈ VD_run | P2 |  |  |  |  |  |
| TC-023 | 2 parallel runs halves required per... | P1 |  |  |  |  |  |
| TC-024 | Derated rating formula: base × DF ×... | P1 |  |  |  |  |  |
| TC-025 | Blue (calculated) cells cannot be e... | P1 |  |  |  |  |  |
| TC-026 | Click FLC blue cell: popup shows co... | P2 |  |  |  |  |  |
| TC-027 | Click reqR blue cell: shows per-run... | P2 |  |  |  |  |  |
| TC-028 | Click VD_run blue cell: shows volta... | P2 |  |  |  |  |  |
| TC-029 | Add Row: new row appears with sensi... | P1 |  |  |  |  |  |
| TC-030 | Delete Row: row removed, remaining ... | P2 |  |  |  |  |  |
| TC-031 | 'Air Temp °C' column visible in Cab... | P1 |  |  |  |  |  |
| TC-032 | Changing Air Temp dropdown updates ... | P1 |  |  |  |  |  |
| TC-033 | Section B FLC matches Cable Schedul... | P1 |  |  |  |  |  |
| TC-034 | Section B shows all 4 derating fact... | P1 |  |  |  |  |  |
| TC-035 | Combined DF = product of all four i... | P1 |  |  |  |  |  |
| TC-036 | Cable size auto-selected from POLYC... | P1 |  |  |  |  |  |
| TC-037 | Section C: VD_run PASS for short ca... | P1 |  |  |  |  |  |
| TC-038 | Section C: VD_start PASS with VFD (... | P1 |  |  |  |  |  |
| TC-039 | Section C: VD_start FAIL for long D... | P1 |  |  |  |  |  |
| TC-040 | Air temp 50°C selected: column 50 h... | P1 |  |  |  |  |  |
| TC-041 | Ground temp 30°C selected: column 3... | P1 |  |  |  |  |  |
| TC-042 | 'In Duct' selected: In Ground row h... | P1 |  |  |  |  |  |
| TC-043 | 'In Air' selected: In Air row highl... | P1 |  |  |  |  |  |
| TC-044 | Section D visible with all 4 laying... | P1 |  |  |  |  |  |
| TC-045 | Section D: In Duct row shows ACTIVE... | P1 |  |  |  |  |  |
| TC-046 | Section D: Underground shows ACTIVE... | P1 |  |  |  |  |  |
| TC-047 | Combined DF verified numerically: F... | P1 |  |  |  |  |  |
| TC-048 | 17 cable sizes visible from 1.5mm² ... | P2 |  |  |  |  |  |
| TC-049 | CU and AL current ratings correct f... | P1 |  |  |  |  |  |
| TC-050 | Impedance R and X values shown for ... | P2 |  |  |  |  |  |
| TC-051 | Admin-only warning banner present; ... | P1 |  |  |  |  |  |
| TC-052 | OC No, Project Name, Revision field... | P2 |  |  |  |  |  |
| TC-053 | Voltage change in Project Inputs pr... | P2 |  |  |  |  |  |
| TC-054 | Motor Calculator and Cable Schedule... | P1 |  |  |  |  |  |
| TC-055 | Derating tab selection reflects in ... | P2 |  |  |  |  |  |
| TC-056 | Maximum cable length 9999m — no cra... | P2 |  |  |  |  |  |
| TC-057 | Non-standard group count interpolat... | P2 |  |  |  |  |  |
| TC-058 | Is/In = 1 (pure VFD): VD_start = VD... | P2 |  |  |  |  |  |
| TC-059 | Very large motor exceeding single-c... | P2 |  |  |  |  |  |
| TC-060 | Rapid sequential field changes — no... | P2 |  |  |  |  |  |